## Overview
Climate Friendly Refrigerants Inventory Workbook (v1)
General Notes
This document is intended to support the initial data collection necessary to build a comprehensive refrigerant inventory, which is the key starting point to implementing a refrigerant management system (RMS), and thus launching your organizations life cycle refrigerant management program. The data points detailed in the 'refrigerant appliance input template' should be collected for all assets containing refrigerants in your organizations facilities. We would advise following the steps outlined below, beginning with identifying the facilities in your portfolio where you intend to track refrigerants. Once your facility by facility inventory is built, it is critical to then begin tracking refrigerant events against that inventory, ideally in an RMS platform. Unlike electricity, refrigerant use is not metered, which means this process is critical to developing an inventory and implementing an RMS for proper tracking, management, and reporting. After all, you can't manage what you don't measure. Please reference the 'RMS FAQ' for additional helpful guidance as well as the 'IIAR inventory calcs' to help determine your refrigerant asset charge sizes if not readily available (these calculations are not limited to ammonia systems only). It is always recommended to work with a certified technician to obtain asset details, especially if charge sizes need to be confirmed by way of system pump down and weighing of the refrigerant.
- New System Startup - It is recommended to input a startup event for new systems, logging any field-installed charge.
- Circuit-Level Tracking - Refrigerant appliances are regulated at the circuit-level and should be tracked in the RMS accordingly -- VRF or distributed systems should be tracked at the condenser level (do not track each indoor unit/evaporator) and systems with multiple circuits should have their service and leak inspections tracked independently.
- Service Data Entry and Timeliness - Service events should be logged in a timely manner to meet recordkeeping requirements and to catch any overdue repairs; ensure that your contractors/service technicians are aware of the information you need at startup, during each service, and at shutdown.
Implementing a Refrigerant Management System - Suggested Order of Operations:
- Determine a list of sites where you will be tracking refrigerants.
- Determine which assets you will be tracking in the RMS.
- Gather asset inventory data (see 'Refrigerant Appliance Input Template' tab).
- Perform quality check and gap analysis on inventory data.
- Import inventory data to RMS.
- Verify asset data in the platform for accuracy and completeness (especially install dates and charge capacities).
- Ensure that service technicians are aware of the records that they must provide you for successful data entry (and train them on the use of the RMS, as applicable).
- Input any historical service event data.
- System is live! Start logging service data and managing inventory directly in the platform!!

## Inventory
Climate Friendly Refrigerants Inventory Workbook. Please refer to 'overview' tab for instructions. |  |  | Existing New | Comfort Cooling ***HVAC*** including comfort cooling and data | Air Dryer / Dehumidifier, Air Handling Unit, Chiller (Centrifugal, Screw, or Scroll), Data/IT Cooling, Heat Pump (Air Source, Water Source, or VRF), Package Unit, Rooftop Unit, Split System - Single, Split System - Multi, Other One line item per refrigerant circuit -- DO NOT report Fan Coils/Evaporators, ONLY Condensers/Outdoor Units | Site name or site code | Specific location on site | Unique identifiers - ideally matched with CMMS or Work Order system; add row(s) and append "_ckt-#" for appliances with multiple circuits. | [5 empty] | BTUH or tons of refrigeration | Can be the same as 'Install Date' if unavailable |  | Normal Operation Disposed/Destroyed Mothballed (Gas Removed, Pending Repair) Moved Planned Retirement Planned Retrofit Provisional Non-Operation Seasonal Operation Seasonal Non-Operation Shutdown/Retired Sold Under Repair |  | Total intended charge/full charge | Input the same as 'Total Charge' if not aware of any difference | Measured Calculated Nameplate | Yes No | High Medium Low Dual Temp Other | Required for 50+ lbs refrigeration systems in California | Optional efficiency info |  |  | Optional electrical info
|  |  |  | Commercial Refrigeration Including ***foodservice*** | Beverage System, Ice Machine, Refrigeration Rack, Reach-In Cooler, Condensing Unit One line item per refrigerant circuit -- DO NOT report Fan Coils/Evaporators, ONLY Condensers/Outdoor Units
|  |  |  | Process Cooling | Chiller, Cooler, Freezer, Lypholizer, Refrigerator, Ultra-low Temp Freezer, Other One line item per refrigerant circuit -- DO NOT report Fan Coils/Evaporators, ONLY Condensers/Outdoor Units
|  |  |  | Refrigerant Inventory Equipment | Gas Recovery Cart, Recovery Cylinder, Virgin Cylinder
System Manager Name | System Manager Email | Region/Division | Existing or New | Asset Sector/Type | Equipment Type (select from the above) | Location | Location Detail | Asset Name | Asset Tag | Manufacturer | Model | Model Year | Serial | Cooling Capacity | Acquired On Date | Install Date | System Status | Refrigerant Type | Gas Capacity (lbs) | Current Gas Weight (lbs) | Charge Capacity Source Type | Has Automatic Leak Detection (ALD) System? | Temperature Classification | Location on Site | SEER | EER | HSPF | Hertz | Volts | Phase | Amps | Notes

## RMS FAQ
Refrigerant Management System - Frequently Asked Questions (FAQs)
Which assets (equipment) need to be added to the inventory? | Given that refrigerant regulations are becoming more stringent and tracking asset data is critical for the development and implementation of refrigerant management strategies, êffecterra recomments tracking data for all refrigerant-containing assets (any type and size) in a refrigerant management system (RMS). If this is not immediately feasible, êffecterra recommends collecting data for all assets above 50 lbs first and then adding smaller assets (at least above 15 lbs) as they are serviced. Note: The minimum threshold for EPA recordkeeping and reporting will expand beyond assets with 50 lbs or more of ozone-depleting (Class II) refrigerants 60 days after the current proposed rules are finalized (likely in early 2025).
How should assets be named/identified? Can an asset’s ‘Name’ be updated? | êffecterra recommends matching the asset ‘Name’ field with any existing equipment number or ID used for other work order or CMMS platforms by facility managers or service technicians. An asset’s name can be updated at any time in a RMS. Previously collected asset ‘Names’ should be reviewed and verified for consistency and accuracy.
Should refrigerant assets be tracked by circuit charges or total charge? | Each refrigerant circuit must be tracked separately. In effect, each circuit is treated as a unit in a RMS, with a unique ‘Name’ and service history (e.g. AC-1_CKT#1, AC-1_CKT #2). Split systems must be tracked at the condenser level, so there should only be one entry (i.e. do not include each evaporator if all are on the same refrigerant circuit).
How should variable refrigerant flow (VRF) systems be tracked? | VRF systems (and all split systems) must be tracked at the condenser level. In VRF systems, the indoor/fan coil units are all on the same refrigerant circuit as the outdoor/condensing unit serving them.
How should an asset’s refrigerant charge be identified? | Accurately determining the charge of a refrigerant system can be challenging as this information is not always readily available. Listed below are different methods for determining the charge in a refrigerant circuit: Measure (best) - The refrigerant charge is removed, weighed, and returned to the system. Calculate (good) - The refrigerant charge is calculated by taking into account the sizes of all system components. A sample calculator is available from the CA Air Resources Board (CARB). Nameplate (acceptable) - This approach simply notes the full “factory charge” of the system listed on the equipment’s nameplate. Note that this approach is less accurate for split (or distributed) systems which often have refrigerant charge added at install due to field-installed piping.
Which types of maintenance/service events need to be recorded? Should all preventative maintenance (PM) events be included? | In general, any service or maintenance event involving the refrigerant circuitry of an asset needs to be tracked. This includes leak inspections, leak repairs, verification tests, refrigerant additions or recovery (for any reason), and ALD calibrations. Initial startup/commissioning and shutdown/disposal for any refrigerant asset must be recorded. Preventative maintenance events only need to be logged in a RMS if it involves a leak inspection or other refrigerant-related service.
Can mechanical contractors/service vendors have access to a RMS and enter service events directly? | This may be possible depending on the platform. If contractors/service vendors are onboarded to enter service data directly into a RMS, it can significantly improve the consistency, accuracy, and timeliness of data entry. This approach should be discussed in depth with stakeholders and should include training on platform use and proper procedures.
Should automatic leak detection (ALD) equipment information be collected and recorded? | Yes. Any automatic leak detection equipment should be recorded in a RMS, including annual calibration service.
When are leak inspections or leak detectors required? | Leak inspection and detection requirements vary depending on location and applicable regulations. See the following links for more information: EPA Refrigerant Management Requirements Overview (USA) CARB RMP Requirements Overview (CA)

## LISTS (hidden)
Dropdown menu (from Refrigerant Appliance Inputs tab) - HIDE THIS BEFORE PUBLICATION!
Existing or New? | Comfort Cooling | Commercial Refrigeration | Process Cooling | Refrigerant Inventory Equipment | System Status | Charge Capacity Source Type | Has Automatic Leak Detection (ALD) System? | Temperature Classification | Refrigerant Type
Existing | Air Dryer / Dehumidifier | Beverage System | Chiller | Gas Recovery Cart | Normal Operation | Measured | Yes | High | CH4
New | Air Handling Unit | Ice Machine | Cooler | Recovery Cylinder | Disposed/Destroyed | Calculated | No | Medium | N2O
| Chiller (Centrifugal, Screw, or Scroll) | Refrigeration Rack | Freezer | Virgin Cylinder | Mothballed (Gas Removed, Pending Repair) | Nameplate |  | Low | R-11
| Data/IT Cooling, Heat Pump (Air Source, Water Source, or VRF) | Reach-In Cooler | Lypholizer |  | Moved |  |  | Dual Temp | R-12
| Package Unit | Condensing Unit | Refrigerator |  | Planned Retirement |  |  | Other | R-123
| Rooftop Unit |  | Ultra-low Temp Freezer |  | Planned Retrofit |  |  |  | R-1233zd(E)
| Split System - Single |  | Other |  | Provisional Non-Operation |  |  |  | R-1234yf
| Split System - Multi |  |  |  | Seasonal Operation |  |  |  | R-1234ze
| Other |  |  |  | Seasonal Non-Operation |  |  |  | R-1234ze(E)
[5 empty] | Shutdown/Retired |  |  |  | R-1234ze(Z)
[5 empty] | Sold |  |  |  | R-124
[5 empty] | Under Repair |  |  |  | R-125
R-13
R-1330(E)
R-1336mzz(Z)
R-134a
R-140
R-141b
R-143a
R-152a
R-22
R-23
R-236fa
R-290
R-32
R-401A
R-401B
R-401C
R-402A
R-402B
R-403A
R-403B
R-404A
R-404C
R-406A
R-407A
R-407B
R-407C
R-407D
R-407E
R-407F
R-408A
R-409A
R-409B
R-410A
R-411B
R-412A
R-413A
R-414A
R-415B
R-416A
R-417A
R-418A
R-419A
R-420A
R-421A
R-422B
R-422D
R-427A
R-438A
R-448A
R-449A
R-452A
R-458A
R-470A
R-500
R-501
R-502
R-503
R-504
R-505
R-506
R-507
R-507A
R-508A
R-508B
R-509A
R-513A
R-514A
R-600A
R-717
R-744
Unknown Refrigerant
Ethylene Glycol
FM 200
Propylene Glycols
SF6
Other - list in 'Notes' column